## Sheet1
S.No | Configuration Menu | Description | Remarks
1 | fid | s.no start with 1 and continues as 1,2,3,4
2 | dev_name | Energy meter/gas meter/ Modbus Device name
3 | esnmart_module | If customer uses Ensmart IO Module it will reflect/else use same dev_name
4 | ip_address | Modbus RS485: 127.0.0.1 Modbus TCP Device; Enter Third party Modbus IP Device name
5 | ip_port | COMPORT 1= 503(Default) COMPROT 2= 504(Default)
6 | slave_id | Modbus Slave id
7 | modbus_type | input_sts= Input Status, coil_sts = Coil Status, hold_read = Holding Register hold_write= Holding Register input_read= Input Register
8 | bacnet_type | ai,bi,ao,bo,av,bv(Depends on Datapoint type as per Modbus slave)
| modbus_type | bacnet_type
| hold_read/input_read | ai or av | ai and bv should state small letter
| hold_write | av or ao | av and ao should state small letter
| coil_sts | bv or bo | bv and bo should state small letter
| input_sts | bi | bi should state small letter
9 | datapoint_name | Bacnet Object Name
11 | modbus_address | please enter extended Modbus Address(1 Based) | ie ., Start Address for Modbus Address is Input Status =100001, Holding Register= 400001, Input Register = 300001, CoilSts = 1
12 | object_id | based on bacnet_type(AI,BI,AO,BO,AV,BV)
|  | AI | BI | AO | BO | AV | BV
|  | AI0 | BI0 | AO0 | BO0 | AV0 | BV0
|  | AI1 | BI1 | AO1 | BO1 | AV1 | BV1
|  | AI2 | BI2 | AO2 | BO2 | AV2 | BV2
|  | AI3 etc., | BI3 etc., | AO3 etc., | BO3 etc., | AV3 etc., | BV3 etc.,
13 | array_name | it is for internal ref , we can ignore and enter any common ref
14 | modbus_index | 0 | for All
15 | array_index | bacnet_type | array_index
|  | AI0 | 0
|  | AI1 | 1
|  | AI2 | 2
|  | BI0 | 0
|  | BI1 | 1
|  | BI2 | 2
|  | BO0 | 0
|  | BO1 | 1
|  | BO2 | 2
|  | BO3 | 3
similar for all bacnet type corresponding array_index we need to add
16 | bit_position | 0 | For coil status and input status
|  | 0,1,2,3 | If Modbus vendor gives values from hold_read or input_read if we need to read it as binary we can use this option
17 | data_type
| binary | enumerated
| float | real
| unsigend integer 16 | unit16
| unsigend integer 32 | unit32
18 | endian
| unit16/32 | LE or BE | Depends on data type Default LE
| float | LE
| Reverse_float | BE
19 | invert
| FALSE | Default Binary will get transfer
| TRUE | Binary value will get Invert from 0 to 1 or 1 to 0
20 | offset | default 0, if any offset to be added we can add to offset received value
21 | gain | Default is 1, If any multiplciation/ division required , factor value need to be entered
22 | plc_address | Internal Referance Keep Default value as A
23 | documentation | Internal Referance Keep Default value as A
Sample File